## Slide 1: Airflow Ventilation System in Operating Rooms
FSC(OT)
ADNAN RAMZAN

## Slide 2: Introduction
Operating Rooms (ORs) require clean air to prevent infections during surgery.
Ventilation helps to control:
Temperature
Pressure
Humidity
Air cleanliness (removes contaminants)

## Slide 3: Purpose of Ventilation in OR
Keeps air free from bacteria and dust.
Maintains a sterile environment.
Provides comfort to doctors and patients.
Prevents spread of infections.

## Slide 4: Airflow Ventilation System
Air flows from ceiling diffusers over the surgical area.
Moves downward and exits near the floor.
Ensures clean-to-dirty airflow pattern.

## Slide 5: Air Changes per Hour (ACH)
ACH = how many times air is replaced in an hour.
ORs usually require:
15–20 ACH (minimum)
20–25 ACH (common)
Up to 40 ACH in advanced systems.
Patient rooms: only 6 ACH needed.

## Slide 6: Methods to Calculate Airflow
1. Area Method
2. Air Change Method
3. Occupancy Method
4. Heat Removal Method

## Slide 7: Area Method
Based on the area (sq. ft.) of the room.
Formula: Airflow (Q) = 1 cfm × Area (sq. ft.)
Example: Bathroom = 60 sq. ft. → Q = 60 cfm

## Slide 8: Air Change Method
Uses number of air changes per hour (ACH).
Formula: Q = (Room Volume × ACH) / 60
Example: For a 2,000 cu. ft. room at 10 ACH → Q = 333 cfm

## Slide 9: Occupancy Method
Based on number of people in the room.
Formula: Q = No. of People × 20 cfm/person
Example: 16 people × 20 = 320 cfm

## Slide 10: Heat Removal Method
Used when temperature control is important.
Formula: Q = (BTU/hr) / (1.08 × ΔT)
BTU/hr = heat load, ΔT = temperature difference
Example: For 9,000 BTU/hr and ΔT = 8°C → Q = 926 cfm

## Slide 11: Airflow System Components
Filters (HEPA) – remove dust and microbes.
Ducts & fans – distribute air.
Return grills – take used air out.
Air handling unit (AHU) – controls temp, humidity, pressure.

## Slide 12: Summary
Clean airflow = infection prevention.
Choose method based on room use.
Maintain correct ACH for safety and comfort.